## Slide 1: ENERGY STORAGE INTEGRATED WITH UK Offshore Wind
Seamus GARVEY
£39.65/MWh

## Slide 2: Contents of this talk
MOTIVATIONS for integrating Energy Storage with OSW
THREE Different classes of solution
The WindTP solution: Challenges and Features
Economics of energy storage integrated with OSW.
Closing Remarks
Medium Duration Energy Storage in the Net Zero UK.

## Slide 3: Contents of this talk
MOTIVATIONS for integrating Energy Storage with OSW
THREE Different classes of solution
The WindTP solution: Challenges and Features
Economics of energy storage integrated with OSW.
Closing Remarks
Medium Duration Energy Storage in the Net Zero UK.

## Slide 4: Motivations: Future energy scenarios
Near-future predictions of future costs for OSW look promising.
Global Offshore Wind Conference London, June 2017
McKinsey Report on Offshore Wind, June 2017
€115/MWh 2010
reduces to €36/MWh 2020 (FID dates)
Be prepared for wind power exceeding all expectations!
Medium Duration Energy Storage in the Net Zero UK.

## Slide 5: Motivations: Future energy scenarios
Be prepared for wind power exceeding all expectations!
From Daniel Laird, Keynote talk at OSES2019, Brest, France, July 2019

## Slide 6: Motivations: Future energy scenarios
Be prepared for wind power exceeding all expectations!
https://cleantechnica.com/2019/09/23/uk-offshore-wind-prices-reach-new-record-low-in-latest-cfd-auction/
Medium Duration Energy Storage in the Net Zero UK.

## Slide 7: Motivations: Why E.S. with Wind?
Demand does not correlate perfectly with availability of wind power.
Electricity Demand
Wind Generation
Solar PV Generation
Demand is seasonal. Wind power is seasonal (and in phase with demand in the UK). PV is in anti-phase.
Medium Duration Energy Storage in the Net Zero UK.

## Slide 8: Motivations: Why E.S. with Wind?
Demand does not correlate perfectly with availability of wind power.
Cardenas et. Al., Energy storage for a high penetration of renewables. OSES2019, Brest, July 2019.
100%
100%
Penetration of Wind (net) 
Penetration of Solar (net) 
Magnitude of storage capacity
to reconcile supply with demand.
With 0% over-capacity
Y2018 needs ~15TWh
Equivalent to 390 hrs
23.6% of all energy consumed has passed through storage.

## Slide 9: Motivations: Why E.S. with Wind?
Demand does not correlate perfectly with availability of wind power.
Cardenas et. Al., Energy storage for a high penetration of renewables. OSES2019, Brest, July 2019.
With a fully-(wind+solar) powered UK,
The capacity of storage required depends on the wind/solar mix AND on the degree of net over-capacity.
Y2018 needs ~4.5TWh with 5% over-generation … around 120 hrs demand.
The optimal ratio of wind/solar changes to 78:22 for 5% over-genn.
21.8% of all energy consumed has passed through storage.

## Slide 10: Motivations: Why E.S. with Wind?
If energy storage is being motivated largely by offshore wind, should it integrated with offshore wind?
Possible improvement in transmission line utilisation
Possible savings in power-conversion equipment
Possible reduction in overall losses
The offshore environment is conducive!
Space, thermal ballast, hydrostatic pressure, easy to manage heavy things
Medium Duration Energy Storage in the Net Zero UK.

## Slide 11: Contents of this talk
MOTIVATIONS for integrating Energy Storage with OSW
THREE Different classes of solution
The WindTP solution: Challenges and Features
Economics of energy storage integrated with OSW.
Closing Remarks
Medium Duration Energy Storage in the Net Zero UK.

## Slide 12: Three DIFFERENT CLASSES
Wind turbines generate electricity, electricity is transformed to something else and back.
Gearbox
Generator
Energy Store (X)
EX
Cnvrtr.
XE
Cnvrtr.
In the best cases, at least the energy store is integrated.
Electricity Consumer
Class #3 ‘Not really integrated at all! “Co-Located”
Direct Consumption
Energy through storage
(??)

## Slide 13: Three DIFFERENT CLASSES
Class #3 ‘Not really integrated at all! “Co-Located”
Wind turbines generate electricity, electricity is transformed to something else and back.
cleantechnica.com/2016/11/14/ge-forges-ahead- worlds-first-wind-hydro-storage-project/
/www.poweronline.com/doc/statoil-launches-batwind-battery-storage-for-offshore-wind-0001
Medium Duration Energy Storage in the Net Zero UK.

## Slide 14: Three DIFFERENT CLASSES
Class #3 ‘Not really integrated at all! “Co-Located”
Wind turbines generate electricity, electricity is transformed to something else and back.
Ian Crossley
Compressed Air Energy Storage for Offshore Wind Turbines. Windpower Monthly. Feb 1, 2018
Proposes storage in an articulated-base “floating wind” type turbine support.

## Slide 15: Three DIFFERENT CLASSES
Rotor power split mechanically between direct generation and conversion to-&-from storage.
Generator
Energy Store (X)
MX
Cnvrtr.
XE
Cnvrtr.
Electricity Consumer
Class #2 Parallel Power conversion
Direct Consumption
Energy through storage
Gearbox
(??)
ME
Medium Duration Energy Storage in the Net Zero UK.

## Slide 16: Three DIFFERENT CLASSES
Class #2 Parallel Power conversion
Rotor power split mechanically between direct generation and conversion to-&-from storage.
Electric
Generator
Energy Storage
System
C Qin, E Innes-Wimsatt & E. Loth. Hydraulic-electric hybrid wind turbines: tower mass savings and energy storage capacity. Renewable Energy, 99, Dec. 2016,
This 2016 paper from University of Virginia proposes a hydraulic transmission with the high-speed end connected simultaneously to an air-compressor/expander and an electrical generator.

## Slide 17: Three DIFFERENT CLASSES
Class #2 Parallel Power conversion
Rotor power split mechanically between direct generation and conversion to-&-from storage.
Electrical Generation Line
Air Compressn/Expansn Line
CN2011104111118A. Prof. Ke Li of Shan Dong University proposes a mechanically-coupled hybrid power take-off with some power being sent directly to generation and some being directed through (compressed air) storage.
Mechanically-coupled mini-type hybrid wind power generating system

## Slide 18: Three DIFFERENT CLASSES
All rotor power is converted to “X” (storable) and then subsequently to electricity.
Energy Store (X)
MX
Cnvrtr.
XE
Cnvrtr.
Electricity Consumer
Class #1 FULLy integrated storage with wind
Direct Consumption
Energy through storage

## Slide 19: Three DIFFERENT CLASSES
All rotor power is converted to “X” (storable) and then subsequently to electricity.
Class #1 FULLy integrated storage with wind
US 2012/0326445 A1, June 2011.
Concept study of wind power utilizing direct thermal energy conversion and thermal energy storage Toru Okazakia, Yasuyuki Shiraib, Taketsune Nakamurab Renewable Energy, 83, 332-338. Nov. 2015
WO 2007/136765 A2. Eric Ingersoll. Wind Turbine System. Compresses air directly

## Slide 20: Three DIFFERENT WAYS
There are three main (thermo-)mechanical options for full integration of energy storage with (onshore or offshore) wind:
Pump water uphill
Compress air
Pump heat
https://spectrum.ieee.org/energy/renewables/ 4-new-ways-to-store-renewable-energy-with-water

## Slide 21: Contents of this talk
MOTIVATIONS for integrating Energy Storage with OSW
THREE Different classes of solution
The WindTP solution: Challenges and Features
Economics of energy storage integrated with OSW.
Closing Remarks
Medium Duration Energy Storage in the Net Zero UK.

## Slide 22: : How IT Works
Start by understanding a hydraulic transmission between main rotor and generator with a high speed ratio ...
WindTP
Hydraulic Pump
Hydraulic Motor
G
… and then replace the hydraulic fluid with a gas!
Generator
Fluid Flow
Medium Duration Energy Storage in the Net Zero UK.

## Slide 23: : How IT Works
is a power transmission system for wind turbines that takes power in directly from the rotor and delivers output power directly to the grid.
WindTP
employs reversible thermal pumping to enable the storage of ~100hrs of rated output capacity at marginal costs much below the cost of the wind turbine itself. This storage capacity with batteries would cost ~25 times as much as the wind turbine.
WindTP
http://multi-science.atypon.com/doi/pdf/10.1260/0309-524X.39.2.149
WindTP

## Slide 24: : How IT Works
Adiabatic compression/expansion of a gas raises/lowers temperature.
Heat can be stored on the “HP” side and coldness can be stored on the “LP” side
Important: “LP” pressure is ~20 bar (2MPa)
“HP” pressure is ~500 bar (50MPa)
Primary Compressor
Expander
Hot Store
Cold Store
HP Side
LP Side
It is the high “LP” pressure is that makes it possible to fit the machine in a wind turbine nacelle.
WindTP

## Slide 25: : How IT Works
WindTP

## Slide 26: The Compressor
WindTP
Multi-stage machine. Each stage has similar Pressure ratio, different temperature.

## Slide 27: The Compressor
WindTP

## Slide 28: The Compressor
WindTP
This is the (4-stage) displacer for a~75kW machine. (~550kg).
Medium Duration Energy Storage in the Net Zero UK.

## Slide 29: The Compressor
WindTP
Previews of the completed machine.
Medium Duration Energy Storage in the Net Zero UK.

## Slide 30: The Compressor
WindTP
Previews of the completed machine.
Medium Duration Energy Storage in the Net Zero UK.

## Slide 31: The Compressor
WindTP
Previews of the completed machine.
Medium Duration Energy Storage in the Net Zero UK.

## Slide 32: Contents of this talk
MOTIVATIONS for integrating Energy Storage with OSW
THREE Different classes of solution
The WindTP solution: Challenges and Features
Economics of energy storage integrated with OSW.
Closing Remarks
Medium Duration Energy Storage in the Net Zero UK.

## Slide 33: Economics of Integrated storage
Overall throughput efficiency: hT = hX  ((1 – ci) + (ci  hS) )
Transmission efficiency: What fraction of input renewable energy (rotor work) is converted to output electricity if not passed through storage
Two Different efficiencies are relevant
hX
Storage efficiency: Ratio between output energy if all passed through storage vs. output energy if none passed through storage.
hS
The fully integrated storage solutions tend to have slightly lower … but a considerably higher value of storage efficiency
hX
hS

## Slide 34: Economics of Integrated storage
Integrated Storage
If high fractions of wind generation will pass through storage, a fully-integrated system will produce more output energy.
http://multi-science.atypon.com/doi/pdf/10.1260/0309-524X.39.2.149
Garvey, Eames et. al. On Generation Integrated Energy Storage Energy Policy 86, 2015, pp544-551
Standalone Storage

## Slide 35: Economics of Integrated storage
It takes only some simple calculations with a spreadsheet to illustrate when the integrated storage solutions are better.
See www.TinyURL.com/ IES_economics

## Slide 36: Economics of Integrated storage

## Slide 37: Economics of Integrated storage

## Slide 38: Contents of this talk
MOTIVATIONS for integrating Energy Storage with OSW
THREE Different classes of solution
The WindTP solution: Challenges and Features
Economics of energy storage integrated with OSW.
Closing Remarks
Medium Duration Energy Storage in the Net Zero UK.

## Slide 39: CLOSING REMARKS
For ALL true integrations of energy storage with wind, yaw bearings are bad! Floating wind turbines may become independent dispatchable power producers in future.
Front Right Buoy (incl. hot store) f28m, H=32m
Front Left Buoy (incl. cold store) f28m, H=32m
Rear Buoy (incl. expndr-gen) f16m, H=19m
10MW system with 1GWh(e) storage.
BYSS* platforms good!
Onboard storage good
Thermal is only option.
Thermal mass = ballast!
* BYSS = Body-Yawing Semi-Submersible

## Slide 40
Thanks for listening.
Seamus.garvey@Nottingham.ac.uk
Acknowledgments: EPSRC & InnoVATe-UK

## Slide 41: BYSS PLATFORMS do not waste sea-space
A single offshore wind turbine installed on a BYSS foundation could “occupy” significant space.

## Slide 42: BYSS PLATFORMS do not waste sea-space
Offshore wind farms never comprise just one turbine..

## Slide 43: Relative sizing of PMGs and
Both Permanent-Magnet Generators (PMGs) and the WindTP machine are sized on torque, T.
WindTP
T  D3 , P  D2  T  P (3/2).
Weight  T (if machine proportions remain the same) (~360 Tons for the SIEMENS 6MW Turbina Sapiens machine … ~3.5MNm torque (?) )
Machine volumes give some sense of the relative sizes:
For PMG machine … the volume of direct interest is the cylinder contained by the airgap.
For WindTP machine … the volume of direct interest is the inlet swept volume.

## Slide 44: Relative sizing of PMGs and
PMG sizing.
WindTP
Airgap shear stress is the determining quantity … ~~50kPa for good PM machines
Torque
WindTP sizing.
Intake pressure (2MPa) and pressure ratio () determine the torque.
Torque

## Slide 45: Relative sizing of PMGs and
Reference Comparison:.
WindTP
Prototype WIndTP machine is rated at 75kW. Total mass of main compressor ~1.5 tons.
VESTAS V17 (75kW) head mass is >6 tons!
Scaling down from SIEMENS (Turbina Sapiens) 6MW machine.
360/(6000/75)1.5 = 0.5 tons 360/(6000/75) = 4.5 tons
Broad conclusion:: WindTP is probably comparable in weight to PMGs at large scales with proper engineering

## Slide 46: Some more Components
WindTP

## Slide 47: Some more Components
WindTP

## Slide 48: Some more Components
WindTP

## Slide 49: Some more Components
WindTP

## Slide 50: Some more Components
WindTP

## Slide 51: Some more Components
WindTP

## Slide 52: Some more Components
WindTP

## Slide 53: Early indications of high compressor efficiency
Preliminary experience with displacer seems very promising
75kW machine ~10m blade tip radius ~10 rad/s.
Rated torque ~7.5kNm. Unloaded loss torque … ~0.2%.
25
20
5
0

## Slide 54: Standalone E.S. systems competing with
Only thermo-mechanical energy-storage solutions can compete as storage with timeframes of 10 – 100 hrs.
WindTP